## FULL HPC SYSTEM
Full HPC System requirements
Proposals will be eliminated and will not be considered for further evaluation for failure to meet any of the following mandatory requirements:
Mandatory Requirement | Bidder’s meets requirement (YES/NO) | Reference page in bidder’s document
a) Bidders must propose the layout as presented in Figure 1, Proposed Floor layout.
b) Biddersmust propose space for 12 racks
c) Bidders must propose space for 12 racks next to each other
d) Bidders must propose a minimum of 725 kW
e) Bidders must propose a minimum of 77.6 kW per rack of compute nodes
f) Bidders must propose direct water cooling for the 8 racks of compute nodes
g) Bidders must propose 4 points (per rack) to connect the racks of the compute nodes
h) Bidders must demonstrate in writing the process of adding extra rack(s) for future expansion in terms of space, power and costs
i) Bidders must propose water cooling with the chemical composition of OAT PG-25 Compute coolant, product code: 18 929
j) Bidders must support Open Network Access (allow external providers to connect into the data centre)
k) Bidders that must propose - Two cross-connect to SANReN/TENET PoP within data centre, or - 20 Gbps manage bandwidth with SLA of at least 99.5% uptime over a month, from the Network working rack to one of the following SANReN/TENET PoPs (duration of contract)
l) Bidders that must propose the layout as presented in Figure 1, Proposed Floor layout.

## BASE HPC SYSTEM
Full HPC System requirements
Proposals will be eliminated and will not be considered for further evaluation for failure to meet any of the following mandatory requirements:
Mandatory Requirement | Bidder’s meets requirement (YES/NO) | Reference page in bidder’s document
a) Bidders must propose the layout as presented in Figure 3, Proposed Floor layout.
b) Bidders must propose space for 7 racks
c) Bidders must propose space for 7 racks next to each other
d) Bidders must propose a minimum of 260 kW
e) Bidders must propose a minimum of 77.6 kW per rack of compute nodes
f) Bidders must propose direct water cooling for the 2 racks of compute nodes
g) Bidders must propose 4 points (per rack) to connect the racks of the compute nodes
h) Bidders must demonstrate in writing the process of adding extra rack(s) for future expansion in terms of space, power and costs
i) Bidders must propose water cooling with the chemical composition of OAT PG-25 Compute coolant, product code: 18 929
j) Bidders that must propose - Two cross-connect to SANReN/TENET PoP within data centre, or - 20 Gbps manage bandwidth with SLA of at least 99.5% uptime over a month, from the Network working rack to one of the following SANReN/TENET PoPs (duration of contract)
k) Bidders must support Open Network Access (allow external providers to connect into the data centre)
l) Bidders must propose the layout as presented in Figure 1, Proposed Floor layout.